## DOC
Disclaimer: | The data presented is the result of a pilot scale based investigation using natural source water and does not reflect the water quality of product water from a full-scale drinking water treatment plant.
Data source must be acknowledged if used in publication.
WQ Change | DOC (mg/L C) Treated Water Feeds | [7 empty] | DOC (mg/L C) PDS Outlet
Period |  | Not Sampled | [8 empty] | Not Sampled
| Sample Date | Raw | Conventional | MF | MIEX/Coag | MIEX/Coag/GAC | MF/NF | Comments | Sample Date | Adjusted Date | Conventional | MIEX/Coag | MIEX/Coag/GAC | MF/NF | Comments
Stable | 2009-07-09 | 4.93 | 3.22 | 3.9 |  |  | 0.34 | Analysis repeated, second set of results used
| 2009-07-31 | 5.81 | 3.54 | 3.76 | 1.98 |  | 0.28
| 2009-08-13 | 4.89 | 3.54 | 3.77 | 2.01 | 0.26 | 0.13 | Results very high, analysis repeated
| 2009-08-17 | 4.83 | 3.64 | 3.69 | 2 | 0.19 | 0.1 | Results very high, analysis repeated
| 2009-08-25 | 4.43 | 3.14 | 3.8 | 2.61 |  | 0.37
| 2009-09-08 | 3.85 | 3.06 | 3.57 | 2 | 0.21 | 0.13
| 2009-09-16 | 3.88 | 2.51 | 3.45 | 1.92 | 0.27 | 0.11
| 2009-09-23 | 3.64 | 2.47 | 3.34 | 1.84 | 0.31 | 0.26 |  |  |  | SP5 sampling not started yet
| 2009-10-01 | [6 empty] | Plant off. New dosing lines being installed
| 2009-10-08 | 4.83 | 3.39 | 3.55 | 1.79 | 0.5 | 0.65
| 2009-10-23 | 4.77 | 2.75 | 3.53 | 2.06 | 0.89 | 0.74 | Irregular sampling due to pipe connection failure
| 2009-10-30 | [6 empty] | Plant failure, no supply
| 2009-11-05 | 3.98 |  | 3.03 | 2.43 | 1.13 | 0.89 | Conventional unavailable, pipe burst
| 2009-11-06 | [6 empty] | Plant in Abeyance due to major PDS failure
| 2010-03-05 | 2.98 | 1.68 | 2.47 | 1 | 0.43 | 0.09
| 2010-03-15 | 3.72 | 1.78 | 2.72 | 1.6 | 0.69 | 0.36
| 2010-03-23 | 3.55 | 1.38 | 2.72 | 1.3 | 0.59 | 0.3
| 2010-03-30 | 3.54 | 1.69 | 2.53 | 1.19 | 0.6 | 0.33
| 2010-04-08 | 3.9 | 2.18 | 3.79 | 1.47 | 1.3
Mannum-Adelaide Pipeline flush | 2010-04-16 | 4.91 | 1.61 | 3.74 | 1.38 | 0.82 | 0.34 | Plant stopped, no supply | 2010-04-19 | 2010-04-16
| 2010-04-20 |  | 2.98 |  | 1.24 | 0.66 | 0.42 |  | 2010-04-23 | 2010-04-20 | 2.33 | 1.81 | 1.58 | 0.78
| 2010-04-27 | 10.87 | 3.06 | 5.34 | 1.98 | 2 | 0.57 | GAC DOC result in question | 2010-04-30 | 2010-04-27 | 2.22 | 1.67 | 1.03 | 1.01
| 2010-05-03 | 7.87 | 2.21 |  | 1.71 | 0.92 | 0.61 |  | 2010-05-06 | 2010-05-03 | 3.84 | 1.83 | 1.18 | 0.91
| 2010-05-10 | 7.62 | 3.16 | 6.32 | 2.15 | 1.16 | 0.66 |  | 2010-05-13 | 2010-05-10 | 3.25 | 2.36 | 1.47 | 0.74
| 2010-05-17 | 8.69 | 3.56 | 6.97 | 2.18 | 1.21 | 0.37 |  | 2010-05-20 | 2010-05-17 | 3.54 | 2.12 | 1.46 | 0.42
| 2010-05-24 | 8.11 | 5.4 | 6.48 | 2.5 | 1.26 | 0.57 |  | 2010-05-27 | 2010-05-24 | 3.64 | 2.35 |  | 0.51 | st1/GAC PDS burst - PDS offline
| 2010-05-31 | 7.32 | 3.53 | 5.47 | 2.12 |  | 0.49 | st1/GAC offline due to PDS burst | 2010-06-03 | 2010-05-31 | 5.11 | 2.27 |  | 0.45
| 2010-06-07 | 7.47 | 4.8 | 5.27 | 2.2 | 1.45 | 1.08 |  | 2010-06-10 | [5 empty] | No sampling Mt P WTP offline, including raw supply
| 2010-06-16 | 6.99 | 2.29 | 4.93 |  |  | 0.42 | mt p st1 offline | 2010-06-19 | 2010-06-16
| 2010-06-21 | [6 empty] | No sampling this week - Mt P st1 offline | 2010-06-24 | 2010-06-21
| 2010-07-05 | 6.28 | 2.71 | 4.78 | 1.88 | 1.12 | 1.96 |  | 2010-07-08 | 2010-07-05
| 2010-07-12 | 5.89 | 3.29 | 5.39 | 1.83 | 1.34 | 0.31 |  | 2010-07-15 | 2010-07-12 | 2.7 | 2.4 | 1.22
| 2010-07-19 | 5.52 | 2.56 | 4.19 | 1.91 | 1.23 | 0.35 |  | 2010-07-22 | 2010-07-19
| 2010-07-26 | 5.3 | 2.85 | 4.21 | 2.05 | 1.49 | 0.38 |  | 2010-07-29 | 2010-07-26 | 3.02 | 1.75 | 1.26 | 0.32
| 2010-08-02 | 5.36 | 2.24 | 4.4 | 1.95 | 1.68 | 0.69 |  | 2010-08-05 | 2010-08-02 | 2.28 | 1.87 | 1.43 | 0.36
| 2010-08-09 | 5.57 | 2.33 | 4.83 | 1.87 | 1.52 | 0.37 |  | 2010-08-12 | 2010-08-09 | 2.05 | 1.69 | 1.35 | 0.99
| 2010-08-16 | 5.79 | 2.38 | 4.64 | 2.35 | 1.75 | 0.47 |  | 2010-08-19 | 2010-08-16 | 2.1 | 2.09 | 1.68 | 0.66
| 2010-08-23 | 5.59 | 2.1 | 4.13 | 1.98 | 1.44 | 0.52 |  | 2010-08-26 | 2010-08-23 | 2.08 | 2.12 | 1.7 | 0.73
| 2010-08-30 | 5.3 | 3.02 | 4.18 | 2.13 | 1.51 | 0.75 |  | 2010-09-02 | 2010-08-30 | 2.64 | 2.07 | 1.61 | 0.59
| 2010-09-07 | 5.75 | 1.85 |  | 1.93 | 1.38 | 0.41 | MF maintenance | 2010-09-10 | 2010-09-07 | 2.55 | 1.76 | 1.3
| 2010-09-13 | [6 empty] | No sampling this week - NF offline | 2010-09-16 | 2010-09-13 |  |  |  |  | No sampling this week- NF offline
| 2010-09-20 | 4.92 | 1.69 | 3.59 | 1.92 | 1.69 | 0.6 |  | 2010-09-23 | 2010-09-20 | 1.55 | 1.68 | 1.53 | 0.58
| 2010-09-28 | 4.62 | 1.83 | 2.97 | 1.48 | 1.17 | 0.43 |  | 2010-10-01 | 2010-09-28 | 1.67 | 1.41 | 1.17 | 0.4
2010 upstream Inflows to River Murray | 2010-10-05 | 7.27 | 2.44 | 5.08 | 1.3 | 1.11 | 0.53 |  | 2010-10-08 | 2010-10-05 |  |  |  |  | All x410 PDS pumps disabled due to poor Conv. WQ
| 2010-10-12 | 9.25 |  | 7.62 | 2.06 | 1.64 | 0.48 | Poor quality water from conventional treatment | 2010-10-15 | 2010-10-12 |  |  |  |  | All x410 PDS pumps disabled due to poor Conv. WQ
| 2010-10-18 | 9.47 | 4.61 | 7.83 | 2.07 | 1.63 | 0.65 |  | 2010-10-21 | 2010-10-18 | 2.42 | 1.46 | 1.19 | 0.2
| 2010-10-25 | 10.8 | 2.99 | 8.29 | 1.83 | 1.31 | 0.24 |  | 2010-10-28 | 2010-10-25 | 4.71 | 1.74 | 1.36 | 0.24
| 2010-11-01 | 13.6 | 4.06 | 10.7 | 2.83 | 1.67 | 0.54 |  | 2010-11-04 | 2010-11-01 | 3.28 | 2.12 | 1.56 | 0.21
| 2010-11-09 | 14.7 | 4.25 | 12.43 | 2.67 | 1.88 | 0.33 |  | 2010-11-12 | 2010-11-09 | 4.94 | 2.68 | 1.82 | 0.32
| 2010-11-16 | 13.5 |  | 11.17 | 3.25 | 2.41 | 0.61 |  | 2010-11-19 | 2010-11-16 |  | 2.92 | 1.81 | 0.25
| 2010-11-23 | 11.53 |  | 9.51 | 3.01 | 2.29 | 0.4 |  | 2010-11-26 | 2010-11-23 |  | 2.76 | 2.09 | 0.28
| 2010-11-29 | 9.81 | 4.19 | 8.43 | 2.86 | 2.01 | 0.68 |  | 2010-11-01 | 2010-10-29
| 2010-12-06 | 11.6 | 5.51 | 9.83 | 3 | 1.96 | 0.52 |  | 2010-12-09 | 2010-12-06 | 5.35 | 2.35 | 1.77 | 0.41
| 2010-12-14 | 11.7 | 5.7 | 10.08 | 2.49 | 2.1 | 0.59 |  | 2010-12-17 | 2010-12-14 | 5.06 | 2.71 | 1.85 | 1.07
| 2010-12-20 | 12.63 | 5.73 | 11.17 | 4.09 | 2.3 | 0.5 |  | 2010-12-23 | 2010-12-20 | 5.01 | 2.23 | 1.75 | 0.29
| 2011-01-04 | 13.1 | 5.01 | 11.27 | 2.99 | 2.52 | 0.66 |  | 2011-01-07 | 2011-01-04 | 4.44 | 3.26 | 2.31 | 0.32
| 2011-01-10 | 14.6 | 5.16 | 12.3 | 4.75 | 2.71 | 0.8 |  | 2011-01-13 | 2011-01-10 | 5.2 | 3.96 | 2.44 | 0.41
| 2011-01-17 | 15.63 | 7.33 | 14 | 5.28 | 3.13 | 0.66 |  | 2011-01-20 | 2011-01-17 | 5.69 | 3.83 | 2.74 | 0.52
| 2011-01-24 | 16.73 | 6.46 | 14.93 | 5.3 | 3.32 | 0.73 |  | 2011-01-27 | 2011-01-24 | 6.35 | 4.26 | 2.65 | 0.43
| 2011-01-31 | 18.53 | 5.93 | 16.43 | 4.67 | 3.83 | 0.44 |  | 2011-02-03 | 2011-01-31 | 5.99 | 4.76 | 3.18 | 0.33
| 2011-02-07 | [6 empty] | PDS pump failures. Plant stopped | 2011-02-10 | 2011-02-07
| 2011-02-15 | 19.1 | 6.66 | 17.1 | 5.66 | 3.45 | 0.78 |  | 2011-02-18 | 2011-02-15
| 2011-02-25 | 18.37 |  | 16 | 5.47 | 3.62 | 0.62 | Poor quality water from conventional treatment | 2011-02-28 | 2011-02-25
| 2011-02-28 | 18.9 | 7.04 | 16.5 | 5.61 | 2.51 | 0.67 |  | 2011-03-03 | 2011-02-28
| 2011-03-07 | 18.83 | 8.79 | 17.27 | 5.53 | 3.98 | 0.47 |  | 2011-03-10 | 2011-03-07 | 5.61 | 4.83 | 3.27 | 0.63
| 2011-03-15 | 17.9 | 7.38 |  | 5.67 | 4.06 |  |  | 2011-03-18 | 2011-03-15
| 2011-03-21 | 16.6 | 6.4 | 13.3 | 4.24 | 3.39 | 1.01 |  | 2011-03-24 | 2011-03-21 | 6.14 | 4.53 | 3.5 | 0.5
| 2011-03-28 | 16.6 | 6.44 | 12.6 | 4.61 | 3.04 | 0.6 |  | 2011-03-31 | 2011-03-28 | 5.4 | 3.92 | 3.04 | 0.54
| 2011-04-04 | 15.43 | 5.18 | 12.6 | 3.68 | 2.63 | 0.4 |  | 2011-04-07 | 2011-04-04 | 5.94 | 3.55 | 3.01 | 0.31
| 2011-04-11 | 16.97 | 5.73 | 12.77 | 4.43 | 3.03 | 0.58 |  | 2011-04-15 | 2011-04-12 | 5.11 | 4.06 | 2.97 | 0.8
| 2011-04-18 | 13.5 | 5.35 | 10.7 | 3.23 | 1.77 | 0.5 |  | 2011-04-21 | 2011-04-18 | 5.46 | 2.88 | 2.51 | 0.4
| 2011-05-02 | 12.5 | 5.5 | 10.67 | 3.54 | 2.61 | 0.43 |  | 2011-05-05 | 2011-05-02 | 4.33 | 3.44 | 2.82 | 0.26
| 2011-05-09 | 11.23 | 5.16 | 9.92 | 4.15 | 3.16 | 0.29 |  | 2011-05-12 | 2011-05-09 | 4.47 | 3.22 | 2.8 | 0.33
| 2011-05-16 | 12.5 | 4.54 | 9.99 | 3.98 | 3.17 | 0.27 |  | 2011-05-19 | 2011-05-16 | 4.71 | 3.72 | 3.11 | 0.27
| 2011-05-23 | 10.83 | 6.31 | 9.46 | 3.04 | 2.21 | 0.34 |  | 2011-05-26 | 2011-05-23 | 4.04 | 3.35 | 3.03 | 0.45
| 2011-05-30 | 10.23 | 5.51 | 9.01 | 3.27 | 2.58 | 0.35 |  | 2011-06-02 | 2011-05-30 | 5.58 | 2.2 | 2.08 | 0.35
| 2011-06-06 | 9.97 | 4.95 | 8.47 | 2.53 | 2.08 | 0.43 |  | 2011-06-09 | 2011-06-06 | 4.85 | 2.64 | 2.48 | 0.33
| 2011-06-14 | 8.98 | 4.09 | 8.33 | 2.75 | 2.02 | 0.56 |  | 2011-06-17 | 2011-06-14 |  |  |  |  | TWS leak plant off
| 2011-06-20 | [6 empty] | TWS leak plant off | 2011-06-23 | 2011-06-20
| 2011-06-27 | [7 empty] | 2011-06-30 | 2011-06-27
| 2011-07-04 | [7 empty] | 2011-07-07 | 2011-07-04
| 2011-07-11 | 7.08 | 2.67 | 5.02 | 1.66 | 1.31 | 0.27 |  | 2011-07-14 | 2011-07-11
| 2011-07-18 | 5.78 | 2.49 | 4.93 | 1.16 | 1.18 | 0.17 |  | 2011-07-21 | 2011-07-18 | 4.14 | 1.58 | 1.28 | 0.4
| 2011-07-25 | 5.15 | 2.12 | 4.37 | 1.24 | 1.24 | 0.3 |  | 2011-07-28 | 2011-07-25 | 2.59 | 1.04 | 1.11 | 0.36
| 2011-08-01 | 5.35 | 2.58 | 4.16 | 1.13 | 1.23 | 0.24 |  | 2011-08-04 | 2011-08-01 | 2.47 | 1.06 | 1.09 | 0.33
Post-Floodwaters | 2011-08-09 | 5.75 | 2.06 | 4.33 | 0.96 | 1.05 | 0.25 |  | 2011-08-12 | 2011-08-09 |  | 1.07 | 1.03 | 0.26
| 2011-08-15 | 5.69 | 2.25 | 4.42 | 1.39 | 1.11 | 0.3 |  | 2011-08-18 | 2011-08-15 | 2.08 | 0.99 | 1.12 | 0.29
| 2011-08-22 | 5.6 | 2.47 | 4.6 | 0.92 | 1.03 | 0.28 |  | 2011-08-25 | 2011-08-22 | 1.75 | 0.98 | 1 | 0.23
| 2011-08-30 | 5.48 | 2.29 | 4.21 | 0.89 | 0.93 | 0.34 |  | 2011-09-02 | 2011-08-30 | 1.56 | 1.03 | 1.02 | 0.29
| 2011-09-05 | 5.69 | 2.64 | 4.44 | 1.07 | 1.04 | 0.37 |  | 2011-09-08 | 2011-09-05
| 2011-09-13 | 6.03 | 2.55 | 6.42 | 1.02 | 1.07 | 0.28 |  | 2011-09-16 | 2011-09-13 | 1.74 | 0.78 | 0.9 | 0.27
| 2011-09-19 | 5.97 | 2.45 | 4.62 | 0.8 | 0.89 | 0.25 |  | 2011-09-22 | 2011-09-19 | 1.76 | 0.82 | 0.94 | 0.32
| 2011-09-26 | 5.72 | 2.28 | 4.57 | 0.78 | 0.88 | 0.2 |  | 2011-09-29 | 2011-09-26 | 1.64 | 0.88 | 0.93 | 0.17
| 2011-10-04 | 7.2 | 2.25 | 5.58 | 1.09 | 1.08 | 1.11 |  | 2011-10-07 | 2011-10-04 | 1.75 | 0.96 | 1.03 | 0.29
| 2011-10-10 | 7.62 | 2.93 | 6.06 | 1.48 | 1.29 | 0.29 |  | 2011-10-13 | 2011-10-10 | 1.66 | 0.97 | 1.03 | 0.28
| 2011-10-17 | 7.42 | 2.71 | 6.21 | 1.21 | 1.08 | 0.24 |  | 2011-10-20 | 2011-10-17 | 1.74 | 1.36 | 1.1 | 0.32
| 2011-10-24 | 7.53 | 3.52 | 6.52 | 1.63 | 1.52 | 0.86 |  | 2011-10-27 | 2011-10-24
| 2011-10-31 | 7.4 | 2.69 | 6.32 | 1.39 | 1.34 | 0.35 |  | 2011-11-03 | 2011-10-31 | 2.2 | 1.02 | 1.16 | 0.34
| 2011-11-07 | 7.25 | 2.8 | 6.1 | 1.69 | 1.63 | 0.42 |  | 2011-11-10 | 2011-11-07 | 2.84 | 1.32 | 1.59 | 0.26
| 2011-11-14 | 6.83 | 3.02 | 6.02 | 1.56 | 1.52 | 0.38 |  | 2011-11-17 | 2011-11-14 | 3.03 | 1.52 | 1.47 | 0.28
| 2011-11-21 | 6.99 | 3.21 | 6.15 | 1.52 | 1.34 | 1.62 |  | 2011-11-24 | 2011-11-21 | 3.09 | 1.39 | 1.53 | 0.59
| 2011-11-28 | 6.67 | 3.62 | 6.09 | 1.64 | 1.4 | 0.26 |  | 2011-12-02 | 2011-11-29 | 3.22 | 1.59 | 1.41 | 0.24
| 2011-12-05 | 6.26 | 2.59 | 5.39 | 1.4 | 1.38 | 0.28 |  | 2011-12-08 | 2011-12-05 | 3.09 | 1.35 | 1.3 | 0.28
| 2011-12-12 | 5.63 | 2.52 | 4.97 | 1.19 | 1.2 | 0.23 |  | 2011-12-15 | 2011-12-12 | 2.71 | 1.32 | 1.26 | 0.44
| 2011-12-19 | 5.53 | 2.62 | 5.15 | 1.62 | 1.49 | 0.26 |  | 2011-12-22 | 2011-12-19 | 2.44 | 1.27 | 1.23 | 0.36
| 2011-12-26 | [7 empty] | 2011-12-29 | 2011-12-26
| 2012-01-02 | 5.81 | 2.44 | 4.96 | 1.14 | 1.57 | 0.53 |  | 2012-01-05 | 2012-01-02 | 2.08 | 1.39 | 1.24 | 0.2
| 2012-01-09 | 5.17 | 2.52 | 4.64 | 0.92 | 1.02 | 0.26 |  | 2012-01-12 | 2012-01-09 | 2.31 | 0.96 | 1.13 | 0.2
| 2012-01-16 | 6.41 | 3.11 | 5.3 | 1 | 1.23 | 0.45 |  | 2012-01-19 | 2012-01-16
| 2012-01-23 | [7 empty] | 2012-01-26 | 2012-01-23
| 2012-01-30 | [7 empty] | 2012-02-02 | 2012-01-30
| 2012-02-06 | 8.74 | 4.97 | 6.26 | 2.02 | 1.61 | 0.31 |  | 2012-02-09 | 2012-02-06
| 2012-02-13 | 7.93 | 4.19 | 6.5 | 2.49 | 1.67 | 0.3 |  | 2012-02-16 | 2012-02-13 | 3.93 | 1.61 | 1.46 | 0.45
| 2012-02-20 | 7.69 | 3.01 | 5.83 | 1.34 | 1.39 | 0.33 |  | 2012-02-23 | 2012-02-20 | 3.11 | 1.42 | 1.47 | 0.22
| 2012-02-27 | 9.08 | 3.47 | 6.76 | 1.62 | 1.39 | 0.71 |  | 2012-03-01 | 2012-02-27 | 3.33 | 1.33 | 1.43 | 0.26
| 2012-03-05 | 8.61 | 3.44 | 7.01 | 2.19 | 1.62 | 0.26 |  | 2012-03-08 | 2012-03-05 | 3.16 | 1.47 | 1.37 | 0.32
| 2012-03-12 | 8.53 | 3.61 | 7.54 | 1.91 | 1.39 | 0.36 |  | 2012-03-15 | 2012-03-12 | 3.21 | 1.33 | 1.24 | 0.29
| 2012-03-19 | 8.99 | 3.57 | 7.94 | 1.82 | 1.4 | 0.24 |  | 2012-03-22 | 2012-03-19 | 3.37 | 1.18 | 1.24 | 0.3
| 2012-03-26 | 9.38 | 4.35 | 8.23 | 1.77 | 1.49 | 0.49 |  | 2012-03-29 | 2012-03-26 | 3.37 | 1.85 | 1.47 | 0.83
| 2012-04-02 | 7.9 | 3.43 | 6.34 | 2.14 | 1.58 | 0.3 |  | 2012-04-05 | 2012-04-02 | 3.85 | 1.58 | 1.4 | 0.43
| 2012-04-09 | 9 | 3.18 | 7.25 | 1.63 | 1.23 | 0.23 |  | 2012-04-12 | 2012-04-09 | 3.55 | 1.37 | 1.17 | 0.23
| 2012-04-16 | 11.6 | 4.42 | 9.14 | 1.26 | 1.38 | 0.38 |  | 2012-04-19 | 2012-04-16 | 4.92 | 1.47 | 1.36 | 0.46
| 2012-04-23 | 12.3 | 4.11 | 10.37 | 2.15 | 1.6 | 0.27 |  | 2012-04-26 | 2012-04-23 | 4.06 | 1.47 | 1.37 | 0.45
| 2012-04-30 | 13.57 | 3.99 | 11.2 | 1.99 | 2.02 | 0.61 |  | 2012-05-03 | 2012-04-30
| 2012-05-07 | 14.53 | 4.16 | 11.57 | 2.5 | 1.7 | 0.35 |  | 2012-05-10 | 2012-05-07
| 2012-05-15 | 14.6 | 4.62 | 12.37 | 2.04 | 1.5 | 0.28 |  | 2012-05-18 | 2012-05-15 | 3.44 | 1.71 | 1.73 | 0.3
| 2012-05-21 | 13.6 | 5.39 | 11.63 | 1.71 | 1.48 | 0.28 |  | 2012-05-24 | 2012-05-21
| 2012-06-04 | 12.13 | 4.48 | 10.09 | 1.94 | 1.54 | 0.36 |  | 2012-06-07 | 2012-06-04 | 3.81 | 1.46 | 1.33 | 0.38
| 2012-06-12 | 11.93 | 4.46 | 10.5 | 2.39 | 1.74 | 0.27 |  | 2012-06-15 | 2012-06-12 | 4.23 | 1.68 | 1.41 | 0.39
| 2012-06-18 | 12.2 | 5.19 | 10.17 | 2.11 | 1.8 | 0.26 |  | 2012-06-21 | 2012-06-18 | 4.12 | 1.69 | 1.55 | 0.36
| 2012-06-25 | 10.3 | 4.13 | 8.61 | 1.51 | 1.22 | 0.25 |  | 2012-06-28 | 2012-06-25 | 4.45 | 2.12 | 2.01 | 0.36
| 2012-07-02 | 9.52 | 4.55 | 8.42 | 2.7 | 1.8 | 0.27 |  | 2012-07-05 | 2012-07-02 | 4.47 | 2.11 | 1.8 | 0.4
| 2012-07-09 | 8.32 | 4.13 | 7.3 | 1.89 | 1.64 | 0.24 |  | 2012-07-12 | 2012-07-09 | 3.39 | 2.21 | 1.84 | 0.3
[9 empty] | 2012-07-19 | 2012-07-16
[9 empty] | 2012-07-26 | 2012-07-23
Formulas:
Adjusted Date = [DOC (mg/L C) PDS Outlet]-3
DOC (mg/L C) Treated Water Feeds = [DOC (mg/L C) Treated Water Feeds, row above]+7

## UV
Disclaimer: | The data presented is the result of a pilot scale based investigation using natural source water and does not reflect the water quality of product water from a full-scale drinking water treatment plant.
Data source must be acknowledged if used in publication.
WQ Change | UV @ 254nm (/cm) Treated Feed | [7 empty] | UV @ 254nm (/cm) PDS Outlet
Period |  | Not Sampled | [8 empty] | Not Sampled
| Sample Date | Raw | Conventional | MF | MIEX/Coag | MIEX/Coag/GAC | MF/NF | Comments | Sample Date | Adjusted Date | Conventional | MIEX/Coag | MIEX/Coag/GAC | MF/NF | Comments
Stable | 2009-07-09 | 0.083 | 0.058 | 0.053 | 0 |  | 0.01 | Analysis repeated, second set of results used
| 2009-07-31 | 0.11 | 0.06 | 0.074 | 0.025 |  | 0.006
| 2009-08-06 | 0.083 | 0.053 | 0.065 | 0.016 | 0 | 0
| 2009-08-10 | 0.083 | 0.06 | 0.067 | 0.021 | 0 | 0
| 2009-08-11 | 0.116 | 0.054 | 0.07 | 0.02 | 0 | 0.001
| 2009-08-13 | 0.107 | 0.058 | 0.072 | 0.021 | 0.002 | 0.006
| 2009-08-17 | 0.112 | 0.066 | 0.072 | 0.026 | 0.006 | 0.007
| 2009-08-25 | 0.117 | 0.05 | 0.068 | 0.021 |  | 0.003
| 2009-09-08 | 0.092 | 0.043 | 0.058 | 0.019 | 0 | 0
| 2009-09-16 | 0.079 | 0.033 | 0.058 | 0.013 | 0 | 0
| 2009-09-23 | 0.082 | 0.038 | 0.065 | 0.02 | 0.004 | 0.005
2009-08-01
| 2009-10-08 | 0.081 | 0.033 | 0.061 | 0.013 | 0 | 0
| 2009-10-23 | 0.079 | 0.048 | 0.055 | 0.015 | 0.007 | 0.004 | Irregular sampling due to pipe connection failure
| 2009-10-30 | [6 empty] | Plant failure, no supply
| 2009-11-05 | 0.065 |  | 0.057 | 0.028 | 0.008 | 0.007 | Conventional unavailable, pipe burst
| 2009-11-06 | [6 empty] | Plant in Abeyance due to major PDS failure
| 2010-03-05 | 0.149 | 0.028 | 0.054 | 0.012 | 0.002 | 0.001
| 2010-03-15 | 0.217 | 0.027 | 0.055 | 0.02 |  | 0.003 | GAC not sampled, pressure testing
| 2010-03-16 |  |  |  |  | 0.004 |  | Only GAC sampled
| 2010-03-30 | 0.168 | 0.025 | 0.051 | 0.013 | 0.003 | 0.003
| 2010-04-08 | 0.283 | 0.028 | 0.075 | 0.013 | 0.006 |  | NF not sampled
| 2010-04-13 | [6 empty] | Plant stopped, no supply
Mannum-Adelaide Pipeline flush | 2010-04-16 | 0.496 | 0.019 | 0.075 | 0.013 | 0.005 | 0.001 | Start of routine monitoring
| 2010-04-20 |  | 0.033 |  | 0.012 | 0.004 | 0.003 |  | 2010-04-23 | 2010-04-20 | 0.021 | 0.01 | 0.004 | 0.003
| 2010-04-27 | 0.351 | 0.058 | 0.125 | 0.021 | 0.011 | 0.009 |  | 2010-04-30 | 2010-04-27 | 0.24 | 0.012 | 0.003 | 0.001
| 2010-05-03 | 0.284 | 0.036 |  | 0.018 | 0.007 | 0.003 |  | 2010-05-06 | 2010-05-03 | 0.071 | 0.017 | 0.007 | 0.005
| 2010-05-10 | 0.346 | 0.058 | 0.184 | 0.026 | 0.011 | 0.006 |  | 2010-05-13 | 2010-05-10 | 0.053 | 0.021 | 0.006 | 0.002
| 2010-05-17 | 0.251 | 0.061 | 0.199 | 0.024 | 0 | 0.001 |  | 2010-05-20 | 2010-05-17 | 0.062 | 0.022 | 0.007 | 0.002
| 2010-05-24 | 0.305 | 0.134 | 0.178 | 0.024 | 0.006 | 0.002 |  | 2010-05-27 | 2010-05-24 | 0.057 | 0.023 |  | 0.001 | st1/GAC offline due to pipe burst
| 2010-05-31 | 0.281 | 0.066 | 0.147 | 0.02 |  | 0 | st1/GAC offline due to pipe burst | 2010-06-03 | 2010-05-31 | 0.097 | 0.024 |  | 0.003 | st1/GAC PDS offline
| 2010-06-07 | 0.299 | 0.108 | 0.135 | 0.019 | 0.008 | 0.001 |  | 2010-06-10 | [5 empty] | No sampling Mt P WTP offline, including raw supply
| 2010-06-16 | 0.361 | 0.033 | 0.133 |  |  | 0.001 | mt p st1 offline
| 2010-06-21 | [6 empty] | No sampling this week - Mt P st1 offline
| 2010-07-05 | 0.339 | 0.047 | 0.111 | 0.019 | 0.009 | 0.002 |  | 2010-07-08 | 2010-07-05 | 0.041
| 2010-07-12 | 0.279 | 0.064 | 0.131 | 0.018 | 0.01 | 0.002 |  | 2010-07-15 | 2010-07-12 | 0.037 | 0.024 | 0.008
| 2010-07-19 | 0.276 | 0.039 | 0.096 | 0.019 | 0.009 | 0.003 |  | 2010-07-22 | 2010-07-19 | 0.05 | 0.028 | 0.015 | 0.002
| 2010-07-26 | 0.27 | 0.048 | 0.102 | 0.02 | 0.01 | 0.002 |  | 2010-07-29 | 2010-07-26 | 0.043 | 0.019 | 0.01 | 0.002
| 2010-08-02 | 0.237 | 0.034 | 0.101 | 0.019 | 0.011 | 0.002 |  | 2010-08-05 | 2010-08-02 | 0.031 | 0.02 | 0.011 | 0.002
| 2010-08-09 | 0.237 | 0.028 | 0.116 | 0.017 | 0.01 | 0.003 |  | 2010-08-12 | 2010-08-09 | 0.024 | 0.016 | 0.011 | 0.003
| 2010-08-16 | 0.21 | 0.023 | 0.094 | 0.018 | 0.009 | 0 |  | 2010-08-19 | 2010-08-16 | 0.026 | 0.018 | 0.011 | 0.002
| 2010-08-23 | 0.174 | 0.028 | 0.088 | 0.018 | 0.01 | 0.004 |  | 2010-08-26 | 2010-08-23 | 0.025 | 0.018 | 0.01 | 0.003
| 2010-08-30 | 0.187 | 0.043 | 0.088 | 0.018 | 0.009 | 0.004 |  | 2010-09-02 | 2010-08-30 | 0.032 | 0.017 | 0.01 | 0.002
| 2010-09-07 | 0.257 | 0.026 |  | 0.019 | 0.01 | 0.001 |  | 2010-09-10 | 2010-09-07 | 0.038 | 0.016 | 0.009 |  | MF Maintenance
| 2010-09-13 | [6 empty] | No sampling this week - NF offline | 2010-09-16 | 2010-09-13 |  |  |  |  | No sampling this week - NF offline
| 2010-09-20 | 0.174 | 0.021 | 0.071 | 0.017 | 0.014 | 0.003 | New NF membrane | 2010-09-23 | 2010-09-20 | 0.018 | 0.014 | 0.009 | 0.002 | New NF Membrane
| 2010-09-28 | 0.206 | 0.027 | 0.069 | 0.015 | 0.009 | 0.002 |  | 2010-10-01 | 2010-09-28 | 0.018 | 0.012 | 0.007 | 0.003
2010 upstream Inflows to River Murray | 2010-10-05 | 0.319 | 0.04 | 0.146 | 0.009 | 0.006 | 0.005 |  | 2010-10-08 | 2010-10-05 |  |  |  |  | All x410 PDS pumps disabled due to poor Conv. WQ
| 2010-10-12 | 0.414 |  | 0.242 | 0.021 | 0.013 | 0.002 |  | 2010-10-15 | 2010-10-12 |  |  |  |  | All x410 PDS pumps disabled due to poor Conv. WQ
| 2010-10-18 | 0.616 | 0.095 | 0.241 | 0.015 | 0.011 | 0.001 |  | 2010-10-21 | 2010-10-18 | 0.037 | 0.017 | 0.009 | 0
| 2010-10-25 | 0.402 | 0.06 | 0.285 | 0.022 | 0.014 | 0.002 |  | 2010-10-28 | 2010-10-25 | 0.101 | 0.015 | 0.008 | 0
| 2010-11-01 | 0.799 | 0.071 | 0.398 | 0.034 | 0.016 | 0.003 |  | 2010-11-04 | 2010-11-01 | 0.057 | 0.026 | 0.016 | 0.007
| 2010-11-09 | 0.722 | 0.073 | 0.468 | 0.03 | 0.016 | 0.003 |  | 2010-11-12 | 2010-11-09 | 0.092 | 0.033 | 0.017 | 0.002
| 2010-11-16 | 0.72 |  | 0.397 | 0.038 | 0.021 | 0.002 |  | 2010-11-19 | 2010-11-16 |  | 0.035 | 0.018 | 0.002
| 2010-11-22 | 0.578 |  | 0.306 | 0.034 | 0.019 | 0.001 |  | 2010-11-25 | 2010-11-22 |  | 0.034 | 0.017 | 0.002
| 2010-11-29 | 0.717 | 0.078 | 0.264 | 0.034 | 0.036 | 0.007 |  | 2010-12-02 | 2010-11-29 |  |  |  |  | Not sampled due to mismatch in PDS retention times
| 2010-12-06 | 0.705 | 0.105 | 0.321 | 0.031 | 0.014 | 0.001 |  | 2010-12-09 | 2010-12-06 | 0.106 | 0.024 | 0.012 | 0.001
| 2010-12-14 | 0.68 | 0.113 | 0.329 | 0.028 | 0.016 | 0.002 |  | 2010-12-17 | 2010-12-14 | 0.097 | 0.029 | 0.014 | 0.002
| 2010-12-20 | 0.658 | 0.099 | 0.372 | 0.045 | 0.019 | 0.005 |  | 2010-12-23 | 2010-12-20 | 0.096 | 0.025 | 0.015 | 0.003
| 2011-01-04 | 0.702 | 0.089 | 0.38 | 0.034 | 0.021 | 0.004 |  | 2011-01-07 | 2011-01-04 | 0.072 | 0.04 | 0.021 | 0.002
| 2011-01-10 | 0.682 | 0.088 | 0.433 | 0.06 | 0.025 | 0.003 |  | 2011-01-13 | 2011-01-10 | 0.084 | 0.042 | 0.023 | 0.003
| 2011-01-17 | 0.716 | 0.145 | 0.477 | 0.062 | 0.025 | 0.002 |  | 2011-01-20 | 2011-01-17 | 0.093 | 0.045 | 0.025 | 0.003
| 2011-01-24 | 0.742 | 0.112 | 0.504 | 0.063 | 0.027 | 0 |  | 2011-01-27 | 2011-01-24 | 0.121 | 0.051 | 0.025 | 0.003
| 2011-01-31 | 0.79 | 0.1 | 0.57 | 0.057 | 0.038 | 0.004 |  | 2011-02-03 | 2011-01-31 | 0.082 | 0.059 | 0.029 | 0.004
| 2011-02-07 | [6 empty] | PDS pump failure plant off | 2011-02-10 | 2011-02-07 |  |  |  |  | PDS pump failure plant off
| 2011-02-15 | 0.68 | 0.117 | 0.565 | 0.06 | 0.028 | 0.006 |  | 2011-02-18 | 2011-02-15 |  |  |  |  | PDS pump failure DS off
| 2011-02-25 | 0.606 |  | 0.515 | 0.061 | 0.031 | 0.006 |  | 2011-02-28 | 2011-02-25
| 2011-02-28 | 0.604 | 0.132 | 0.514 | 0.063 | 0.019 | 0.008 |  | 2011-03-03 | 2011-02-28
| 2011-03-07 | 0.609 | 0.166 | 0.56 | 0.061 | 0.036 | 0.008 |  | 2011-03-10 | 2011-03-07 | 0.085 | 0.053 | 0.028 | 0.008
| 2011-03-15 | 0.575 | 0.121 |  | 0.053 | 0.033 |  | NF membrane failure | 2011-03-18 | 2011-03-15 |  |  |  |  | Plant off due to FWS work
| 2011-03-21 | 0.467 | 0.114 | 0.361 | 0.041 | 0.028 | 0.009 |  | 2011-03-24 | 2011-03-21 | 0.093 | 0.047 | 0.031 | 0.007
| 2011-03-28 | 0.493 | 0.099 | 0.345 | 0.043 | 0.02 | 0.007 |  | 2011-03-31 | 2011-03-28 | 0.067 | 0.036 | 0.022 | 0.006
| 2011-04-04 | 0.533 | 0.086 | 0.356 | 0.035 | 0.021 | 0.003 |  | 2011-04-07 | 2011-04-04 | 0.076 | 0.032 | 0.024 | 0.003
| 2011-04-11 | 0.427 | 0.077 | 0.362 | 0.033 | 0.025 | 0.001 |  | 2011-04-15 | 2011-04-12 | 0.074 | 0.039 | 0.024 | 0.002
| 2011-04-18 | 0.484 | 0.088 | 0.276 | 0.031 | 0.013 | 0.006 |  | 2011-04-21 | 2011-04-18 | 0.084 | 0.027 | 0.019 | 0.002
| 2011-05-02 | 0.346 | 0.09 | 0.284 | 0.029 | 0.016 | 0.001 |  | 2011-05-05 | 2011-05-02 | 0.067 | 0.036 | 0.024 | 0.004
| 2011-05-09 | 0.356 | 0.081 | 0.27 | 0.048 | 0.028 | 0.003 | Chlorine dosing at MIEX/Coag flash mixer turned off | 2011-05-12 | 2011-05-09 | 0.067 | 0.035 | 0.026 | 0.003
| 2011-05-16 | 0.311 | 0.069 | 0.264 | 0.044 | 0.03 | 0.002 |  | 2011-05-19 | 2011-05-16 | 0.068 | 0.042 | 0.03 | 0.005
| 2011-05-23 | 0.351 | 0.111 | 0.247 | 0.031 | 0.018 | 0.002 |  | 2011-05-26 | 2011-05-23 | 0.053 | 0.035 | 0.027 | 0.003
| 2011-05-30 | 0.334 | 0.094 | 0.234 | 0.037 | 0.022 | 0.003 |  | 2011-06-02 | 2011-05-30 | 0.083 | 0.019 | 0.015 | 0.002
| 2011-06-06 | 0.38 | 0.079 | 0.203 | 0.025 | 0.018 | 0.004 |  | 2011-06-09 | 2011-06-06 | 0.067 | 0.025 | 0.021 | 0.004
| 2011-06-14 | 0.326 | 0.064 | 0.204 | 0.029 | 0.018 | 0.003 |  | 2011-06-17 | 2011-06-14 |  |  |  |  | Treated water storage drained, WTP off 1 week
| 2011-06-20 | [6 empty] | TWS leak plant off
2011-06-27
2011-07-04
2011-07-11
| 2011-07-18 | 0.193 | 0.039 | 0.131 | 0.01 | 0.01 | 0.001 |  | 2011-07-21 | 2011-07-18 | 0.058 | 0.011 | 0.006 | 0
| 2011-07-25 | 0.187 | 0.032 | 0.123 | 0.01 | 0.009 | 0.002 |  | 2011-07-28 | 2011-07-25 | 0.035 | 0.007 | 0.007 | 0.003
| 2011-08-01 | 0.209 | 0.04 | 0.1 | 0.009 | 0.009 | 0.002 |  | 2011-08-04 | 2011-08-01 | 0.031 | 0.007 | 0.007 | 0.002
| 2011-08-09 | 0.227 | 0.031 | 0.114 | 0.01 | 0.01 | 0.003 |  | 2011-08-12 | 2011-08-09 |  | 0.007 | 0.012 | 0.003
| 2011-08-15 | 0.237 | 0.035 | 0.118 | 0.015 | 0.009 | 0.001 |  | 2011-08-18 | 2011-08-15 | 0.028 | 0.007 | 0.008 | 0.001
| 2011-08-22 | 0.242 | 0.038 | 0.125 | 0.006 | 0.006 | 0.003 |  | 2011-08-25 | 2011-08-22 | 0.022 | 0.008 | 0.007 | 0.002
| 2011-08-30 | 0.256 | 0.038 | 0.12 | 0.007 | 0.007 | 0.001 |  | 2011-09-02 | 2011-08-30 | 0.019 | 0.009 | 0.007 | 0.002
| 2011-09-05 | 0.256 | 0.045 | 0.127 | 0.01 | 0.009 | 0.002 |  | 2011-09-08 | 2011-09-05
| 2011-09-13 | 0.287 | 0.044 | 0.137 | 0.01 | 0.01 | 0.002 |  | 2011-09-16 | 2011-09-13 | 0.021 | 0.005 | 0.005 | 0.001
| 2011-09-19 | 0.243 | 0.039 | 0.135 | 0.005 | 0.006 | 0 |  | 2011-09-22 | 2011-09-19 | 0.021 | 0.006 | 0.006 | 0.001
| 2011-09-26 | 0.284 | 0.037 | 0.131 | 0.005 | 0.005 | 0 |  | 2011-09-29 | 2011-09-26 | 0.022 | 0.009 | 0.007 | 0.002
| 2011-10-04 | 0.266 | 0.037 | 0.173 | 0.009 | 0.008 | 0.002 |  | 2011-09-07 | 2011-09-04 | 0.021 | 0.008 | 0.007 | 0.002
| 2011-10-10 | 0.366 | 0.057 | 0.188 | 0.016 | 0.016 | 0.002 |  | 2011-10-13 | 2011-10-10 | 0.02 | 0.011 | 0.009 | 0.002
| 2011-10-17 | 0.314 | 0.047 | 0.192 | 0.013 | 0.009 | 0.002 |  | 2011-10-20 | 2011-10-17 | 0.021 | 0.012 | 0.008 | 0.002
| 2011-10-25 | 0.3 | 0.062 | 0.191 | 0.014 | 0.011 | 0.002 |  | 2011-10-28 | 2011-10-25
| 2011-10-31 | 0.262 | 0.044 | 0.184 | 0.014 | 0.011 | 0.002 |  | 2011-11-03 | 2011-10-31 | 0.03 | 0.01 | 0.008 | 0.003
| 2011-11-07 | 0.28 | 0.044 | 0.186 | 0.017 | 0.013 | 0.002 |  | 2011-11-10 | 2011-11-07 | 0.041 | 0.011 | 0.013 | 0.002
| 2011-11-14 | 0.236 | 0.053 | 0.179 | 0.018 | 0.014 | 0.003 |  | 2011-11-17 | 2011-11-14 | 0.045 | 0.016 | 0.014 | 0.003
| 2011-11-21 | 0.259 | 0.056 | 0.172 | 0.015 | 0.011 | 0.005 |  | 2011-11-24 | 2011-11-21 | 0.047 | 0.013 | 0.011 | 0.004
| 2011-11-28 | 0.2 | 0.065 | 0.168 | 0.016 | 0.013 | 0.002 |  | 2011-12-02 | 2011-11-29 | 0.051 | 0.017 | 0.013 | 0.003
| 2011-12-05 | 0.213 | 0.04 | 0.149 | 0.015 | 0.013 | 0.002 |  | 2011-12-08 | 2011-12-05 | 0.048 | 0.013 | 0.011 | 0.002
| 2011-12-12 | 0.177 | 0.039 | 0.136 | 0.012 | 0.01 | 0.002 |  | 2011-12-15 | 2011-12-12 | 0.038 | 0.011 | 0.009 | 0.003
| 2011-12-19 | 0.152 | 0.041 | 0.137 | 0.018 | 0.011 | 0.002 |  | 2011-12-22 | 2011-12-19 | 0.036 | 0.013 | 0.01 | 0.002
| 2011-12-26 | [7 empty] | 2011-12-29 | 2011-12-26
| 2012-01-02 | 0.179 | 0.037 | 0.129 | 0.009 | 0.016 | 0.002 |  | 2012-01-05 | 2012-01-02 | 0.031 | 0.015 | 0.011 | 0.001
| 2012-01-09 | 0.161 | 0.043 | 0.125 | 0.008 | 0.008 | 0.001 |  | 2012-01-12 | 2012-01-09 | 0.034 | 0.009 | 0.009 | 0.001
| 2012-01-16 | 0.139 | 0.046 | 0.132 | 0.005 | 0.009 | 0.003 |  | 2012-01-19 | 2012-01-16
| 2012-01-23 | [7 empty] | 2012-01-26 | 2012-01-23
| 2012-01-30 | [7 empty] | 2012-02-02 | 2012-01-30
| 2012-02-06 | 0.163 | 0.073 | 0.148 | 0.013 | 0.011 | 0.001 |  | 2012-02-09 | 2012-02-06
| 2012-02-13 | 0.198 | 0.067 | 0.157 | 0.027 | 0.012 | 0.001 |  | 2012-02-16 | 2012-02-13 | 0.056 | 0.015 | 0.01 | 0.001
| 2012-02-20 | 0.221 | 0.053 | 0.201 | 0.013 | 0.013 | 0.003 |  | 2012-02-23 | 2012-02-20 | 0.045 | 0.014 | 0.012 | 0.004
| 2012-02-27 | 0.276 | 0.06 | 0.221 | 0.014 | 0.013 | 0.003 |  | 2012-03-01 | 2012-02-27 | 0.054 | 0.012 | 0.01 | 0
| 2012-03-05 | 0.304 | 0.058 | 0.21 | 0.026 | 0.015 | 0.002 |  | 2012-03-08 | 2012-03-05 | 0.048 | 0.015 | 0.01 | 0.002
| 2012-03-12 | 0.422 | 0.064 | 0.212 | 0.013 | 0.012 | 0.002 |  | 2012-03-15 | 2012-03-12 | 0.048 | 0.013 | 0.009 | 0.003
| 2012-03-19 | 0.302 | 0.061 | 0.216 | 0.013 | 0.011 | 0.002 |  | 2012-03-22 | 2012-03-19 | 0.052 | 0.01 | 0.008 | 0.002
| 2012-03-26 | 0.275 | 0.075 | 0.228 | 0.017 | 0.013 | 0.003 |  | 2012-03-29 | 2012-03-26 | 0.053 | 0.017 | 0.011 | 0.003
| 2012-04-02 | 0.303 | 0.059 | 0.179 | 0.023 | 0.012 | 0.001 |  | 2012-04-05 | 2012-04-02 | 0.066 | 0.018 | 0.012 | 0.004
| 2012-04-09 | 0.334 | 0.057 | 0.228 | 0.016 | 0.009 | 0.001 |  | 2012-04-12 | 2012-04-09 | 0.057 | 0.013 | 0.01 | 0.001
| 2012-04-16 | 0.52 | 0.085 | 0.322 | 0.012 | 0.011 | 0.002 |  | 2012-04-19 | 2012-04-16 | 0.102 | 0.016 | 0.013 | 0.002
| 2012-04-23 | 0.528 | 0.074 | 0.382 | 0.026 | 0.015 | 0.002 |  | 2012-04-26 | 2012-04-23 | 0.079 | 0.016 | 0.01 | 0.003
| 2012-04-30 | 0.57 | 0.072 | 0.413 | 0.02 | 0.014 | 0.002 |  | 2012-05-03 | 2012-04-30
| 2012-05-07 | 0.471 | 0.074 | 0.408 | 0.031 | 0.014 | 0.004 |  | 2012-05-10 | 2012-05-07
| 2012-05-15 | 0.502 | 0.072 | 0.416 | 0.021 | 0.012 | 0.003 |  | 2012-05-18 | 2012-05-15 | 0.063 | 0.021 | 0.014 | 0.003
| 2012-05-21 | 0.459 | 0.097 | 0.408 | 0.018 | 0.013 | 0.002 |  | 2012-05-24 | 2012-05-21
| 2012-06-04 | 0.449 | 0.085 | 0.379 | 0.021 | 0.015 | 0.008 |  | 2012-06-07 | 2012-06-04 | 0.064 | 0.016 | 0.012 | 0.005
| 2012-06-12 | 0.456 | 0.082 | 0.274 | 0.03 | 0.017 | 0.006 |  | 2012-06-15 | 2012-06-12 | 0.076 | 0.018 | 0.013 | 0.008
| 2012-06-18 | 0.403 | 0.099 | 0.359 | 0.025 | 0.019 | 0.004 |  | 2012-06-21 | 2012-06-18 | 0.073 | 0.02 | 0.014 | 0.006
| 2012-06-25 | 0.307 | 0.074 | 0.262 | 0.015 | 0.011 | 0.003 |  | 2012-06-28 | 2012-06-25 | 0.074 | 0.023 | 0.018 | 0.003
| 2012-07-02 | 0.306 | 0.083 | 0.251 | 0.033 | 0.018 | 0.003 |  | 2012-07-05 | 2012-07-02 | 0.075 | 0.023 | 0.016 | 0.003
| 2012-07-09 | 0.245 | 0.071 | 0.223 | 0.019 | 0.014 | 0.002 |  | 2012-07-12 | 2012-07-09 | 0.051 | 0.023 | 0.018 | 0.003
| 2012-07-16 | 0.239 | 0.064 | 0.21 | 0.013 | 0.012 | 0.003 |  | 2012-07-19 | 2012-07-16 | 0.055 | 0.017 | 0.012 | 0.006
| 2012-07-23 | 0.232 | 0.051 | 0.18 | 0.037 | 0.023 | 0.003 |  | 2012-07-26 | 2012-07-23 | 0.051 | 0.017 | 0.013 | 0.004
| 2012-07-31 | 0.188 | 0.038 | 0.145 | 0.024 | 0.014 | 0.004
Formulas:
Adjusted Date = [UV @ 254nm (/cm) PDS Outlet]-3
UV @ 254nm (/cm) Treated Feed = [UV @ 254nm (/cm) Treated Feed, row above]+7

## SUVA
Disclaimer: | The data presented is the result of a pilot scale based investigation using natural source water and does not reflect the water quality of product water from a full-scale drinking water treatment plant.
Data source must be acknowledged if used in publication.
WQ Change
Period | UV @ 254nm (/cm) | [6 empty] | DOC (mg/L C) | [6 empty] | SUVA (/m/mg/L)
| Sample Date | Raw | Conventional | MF | MIEX/Coag | MIEX/Coag/GAC | MF/NF | Sample Date | Raw | Conventional | MF | MIEX/Coag | MIEX/Coag/GAC | MF/NF | Sample Date | Raw | Conventional | MF | MIEX/Coag | MIEX/Coag/GAC | MF/NF
Stable | 2009-07-09 | 0.083 | 0.058 | 0.053 |  |  | 0.01 | 2009-07-09 | 4.93 | 3.22 | 3.9 |  |  | 0.34 | 2009-07-09 | 1.6836 | 1.8012 | 1.359 |  |  | 2.9412
| 2009-07-31 | 0.11 | 0.06 | 0.074 | 0.025 |  | 0.006 | 2009-07-31 | 5.81 | 3.54 | 3.76 | 1.98 |  | 0.28 | 2009-07-31 | 1.8933 | 1.6949 | 1.9681 | 1.2626 |  | 2.1429
| 2009-08-06 | 0.083 | 0.053 | 0.065 | 0.016 | 0 | 0 | 2009-08-06 | [6 empty] | 2009-08-06
| 2009-08-10 | 0.083 | 0.06 | 0.067 | 0.021 | 0 | 0 | 2009-08-10 | [6 empty] | 2009-08-10
| 2009-08-11 | 0.116 | 0.054 | 0.07 | 0.02 | 0 | 0.001 | 2009-08-11 | [6 empty] | 2009-08-11
| 2009-08-13 | 0.107 | 0.058 | 0.072 | 0.021 | 0.002 | 0.006 | 2009-08-13 | 4.89 | 3.54 | 3.77 | 2.01 | 0.26 | 0.13 | 2009-08-13 | 2.1881 | 1.6384 | 1.9098 | 1.0448 | 0.76923 | 4.6154
| 2009-08-17 | 0.112 | 0.066 | 0.072 | 0.026 | 0.006 | 0.007 | 2009-08-17 | 4.83 | 3.64 | 3.69 | 2 | 0.19 | 0.1 | 2009-08-17 | 2.3188 | 1.8132 | 1.9512 | 1.3 | 3.1579 | 7
| 2009-08-25 | 0.117 | 0.05 | 0.068 | 0.021 |  | 0.003 | 2009-08-25 | 4.43 | 3.14 | 3.8 | 2.61 |  | 0.37 | 2009-08-25 | 2.6411 | 1.5924 | 1.7895 | 0.8046 |  | 0.81081
| 2009-09-08 | 0.092 | 0.043 | 0.058 | 0.019 | 0 | 0 | 2009-09-08 | 3.85 | 3.06 | 3.57 | 2 | 0.21 | 0.13 | 2009-09-08 | 2.3896 | 1.4052 | 1.6246 | 0.95 | 0 | 0
| 2009-09-16 | 0.079 | 0.033 | 0.058 | 0.013 | 0 | 0 | 2009-09-16 | 3.88 | 2.51 | 3.45 | 1.92 | 0.27 | 0.11 | 2009-09-16 | 2.0361 | 1.3147 | 1.6812 | 0.67708 | 0 | 0
| 2009-09-23 | 0.082 | 0.038 | 0.065 | 0.02 | 0.004 | 0.005 | 2009-09-23 | 3.64 | 2.47 | 3.34 | 1.84 | 0.31 | 0.26 | 2009-09-23 | 2.2527 | 1.5385 | 1.9461 | 1.087 | 1.2903 | 1.9231
| 2009-08-01 | [6 empty] | 2009-10-01 | [6 empty] | 2009-10-01
| 2009-10-08 | 0.081 | 0.033 | 0.061 | 0.013 | 0 | 0 | 2009-10-08 | 4.83 | 3.39 | 3.55 | 1.79 | 0.5 | 0.65 | 2009-10-08 | 1.677 | 0.97345 | 1.7183 | 0.72626 | 0 | 0
| 2009-10-23 | 0.079 | 0.048 | 0.055 | 0.015 | 0.007 | 0.004 | 2009-10-23 | 4.77 | 2.75 | 3.53 | 2.06 | 0.89 | 0.74 | 2009-10-23 | 1.6562 | 1.7455 | 1.5581 | 0.72816 | 0.78652 | 0.54054
| 2009-10-30 | [6 empty] | 2009-10-30 | [6 empty] | 2009-10-30
| 2009-11-05 | 0.065 |  | 0.057 | 0.028 | 0.008 | 0.007 | 2009-11-05 | 3.98 |  | 3.03 | 2.43 | 1.13 | 0.89 | 2009-11-05 | 1.6332 |  | 1.8812 | 1.1523 | 0.70796 | 0.78652
| 2009-11-06 | [6 empty] | 2009-11-06 | [6 empty] | 2009-11-06
| 2010-03-05 | 0.149 | 0.028 | 0.054 | 0.012 | 0.002 | 0.001 | 2010-03-05 | 2.98 | 1.68 | 2.47 | 1 | 0.43 | 0.09 | 2010-03-05 | 5 | 1.6667 | 2.1862 | 1.2 | 0.46512 | 1.1111
| 2010-03-15 | 0.217 | 0.027 | 0.055 | 0.02 |  | 0.003 | 2010-03-15 | 3.72 | 1.78 | 2.72 | 1.6 | 0.69 | 0.36 | 2010-03-15 | 5.8333 | 1.5169 | 2.0221 | 1.25 | 0 | 0.83333
| 2010-03-16 |  |  |  |  | 0.004 |  | 2010-03-16 | [6 empty] | 2010-03-16
| 2010-03-23 | [6 empty] | 2010-03-23 | 3.55 | 1.38 | 2.72 | 1.3 | 0.59 | 0.3 | 2010-03-23
| 2010-03-30 | 0.168 | 0.025 | 0.051 | 0.013 | 0.003 | 0.003 | 2010-03-30 | 3.54 | 1.69 | 2.53 | 1.19 | 0.6 | 0.33 | 2010-03-30 | 4.7458 | 1.4793 | 2.0158 | 1.0924 | 0.5 | 0.90909
| 2010-04-08 | 0.283 | 0.028 | 0.075 | 0.013 | 0.006 |  | 2010-04-08 | 3.9 | 2.18 | 3.79 | 1.47 | 1.3 |  | 2010-04-08 | 7.2564 | 1.2844 | 1.9789 | 0.88435 | 0.46154
| 2010-04-13 | [6 empty] | 2010-04-13 | [6 empty] | 2010-04-13
Mannum-Adelaide Pipeline flush | 2010-04-16 | 0.496 | 0.019 | 0.075 | 0.013 | 0.005 | 0.001 | 2010-04-16 | 4.91 | 1.61 | 3.74 | 1.38 | 0.82 | 0.34 | 2010-04-16 | 10.1018 | 1.1801 | 2.0053 | 0.94203 | 0.60976 | 0.29412
| 2010-04-20 |  | 0.033 |  | 0.012 | 0.004 | 0.003 | 2010-04-20 |  | 2.98 |  | 1.24 | 0.66 | 0.42 | 2010-04-20 |  | 1.1074 |  | 0.96774 | 0.60606 | 0.71429
| 2010-04-27 | 0.351 | 0.058 | 0.125 | 0.021 | 0.011 | 0.009 | 2010-04-27 | 10.87 | 3.06 | 5.34 | 1.98 | 2 | 0.57 | 2010-04-27 | 3.2291 | 1.8954 | 2.3408 | 1.0606 | 0.55 | 1.5789
| 2010-05-03 | 0.284 | 0.036 |  | 0.018 | 0.007 | 0.003 | 2010-05-03 | 7.87 | 2.21 |  | 1.71 | 0.92 | 0.61 | 2010-05-03 | 3.6086 | 1.629 |  | 1.0526 | 0.76087 | 0.4918
| 2010-05-10 | 0.346 | 0.058 | 0.184 | 0.026 | 0.011 | 0.006 | 2010-05-10 | 7.62 | 3.16 | 6.32 | 2.15 | 1.16 | 0.66 | 2010-05-10 | 4.5407 | 1.8354 | 2.9114 | 1.2093 | 0.94828 | 0.90909
| 2010-05-17 | 0.251 | 0.061 | 0.199 | 0.024 | 0 | 0.001 | 2010-05-17 | 8.69 | 3.56 | 6.97 | 2.18 | 1.21 | 0.37 | 2010-05-17 | 2.8884 | 1.7135 | 2.8551 | 1.1009 | 0 | 0.27027
| 2010-05-24 | 0.305 | 0.134 | 0.178 | 0.024 | 0.006 | 0.002 | 2010-05-24 | 8.11 | 5.4 | 6.48 | 2.5 | 1.26 | 0.57 | 2010-05-24 | 3.7608 | 2.4815 | 2.7469 | 0.96 | 0.47619 | 0.35088
| 2010-05-31 | 0.281 | 0.066 | 0.147 | 0.02 |  | 0 | 2010-05-31 | 7.32 | 3.53 | 5.47 | 2.12 |  | 0.49 | 2010-05-31 | 3.8388 | 1.8697 | 2.6874 | 0.9434 |  | 0
| 2010-06-07 | 0.299 | 0.108 | 0.135 | 0.019 | 0.008 | 0.001 | 2010-06-07 | 7.47 | 4.8 | 5.27 | 2.2 | 1.45 | 1.08 | 2010-06-07 | 4.0027 | 2.25 | 2.5617 | 0.86364 | 0.55172 | 0.092593
| 2010-06-16 | 0.361 | 0.033 | 0.133 |  |  | 0.001 | 2010-06-16 | 6.99 | 2.29 | 4.93 |  |  | 0.42 | 2010-06-16 | 5.1645 | 1.441 | 2.6978 |  |  | 0.2381
| 2010-06-21 | [6 empty] | 2010-06-21 | [6 empty] | 2010-06-21
| 2010-07-05 | 0.339 | 0.047 | 0.111 | 0.019 | 0.009 | 0.002 | 2010-07-05 | 6.28 | 2.71 | 4.78 | 1.88 | 1.12 | 1.96 | 2010-07-05 | 5.3981 | 1.7343 | 2.3222 | 1.0106 | 0.80357 | 0.10204
| 2010-07-12 | 0.279 | 0.064 | 0.131 | 0.018 | 0.01 | 0.002 | 2010-07-12 | 5.89 | 3.29 | 5.39 | 1.83 | 1.34 | 0.31 | 2010-07-12 | 4.7368 | 1.9453 | 2.4304 | 0.98361 | 0.74627 | 0.64516
| 2010-07-19 | 0.276 | 0.039 | 0.096 | 0.019 | 0.009 | 0.003 | 2010-07-19 | 5.52 | 2.56 | 4.19 | 1.91 | 1.23 | 0.35 | 2010-07-19 | 5 | 1.5234 | 2.2912 | 0.99476 | 0.73171 | 0.85714
| 2010-07-26 | 0.27 | 0.048 | 0.102 | 0.02 | 0.01 | 0.002 | 2010-07-26 | 5.3 | 2.85 | 4.21 | 2.05 | 1.49 | 0.38 | 2010-07-26 | 5.0943 | 1.6842 | 2.4228 | 0.97561 | 0.67114 | 0.52632
| 2010-08-02 | 0.237 | 0.034 | 0.101 | 0.019 | 0.011 | 0.002 | 2010-08-02 | 5.36 | 2.24 | 4.4 | 1.95 | 1.68 | 0.69 | 2010-08-02 | 4.4216 | 1.5179 | 2.2955 | 0.97436 | 0.65476 | 0.28986
| 2010-08-09 | 0.237 | 0.028 | 0.116 | 0.017 | 0.01 | 0.003 | 2010-08-09 | 5.57 | 2.33 | 4.83 | 1.87 | 1.52 | 0.37 | 2010-08-09 | 4.2549 | 1.2017 | 2.4017 | 0.90909 | 0.65789 | 0.81081
| 2010-08-16 | 0.21 | 0.023 | 0.094 | 0.018 | 0.009 | 0 | 2010-08-16 | 5.79 | 2.38 | 4.64 | 2.35 | 1.75 | 0.47 | 2010-08-16 | 3.6269 | 0.96639 | 2.0259 | 0.76596 | 0.51429 | 0
| 2010-08-23 | 0.174 | 0.028 | 0.088 | 0.018 | 0.01 | 0.004 | 2010-08-23 | 5.59 | 2.1 | 4.13 | 1.98 | 1.44 | 0.52 | 2010-08-23 | 3.1127 | 1.3333 | 2.1308 | 0.90909 | 0.69444 | 0.76923
| 2010-08-30 | 0.187 | 0.043 | 0.088 | 0.018 | 0.009 | 0.004 | 2010-08-30 | 5.3 | 3.02 | 4.18 | 2.13 | 1.51 | 0.75 | 2010-08-30 | 3.5283 | 1.4238 | 2.1053 | 0.84507 | 0.59603 | 0.53333
| 2010-09-07 | 0.257 | 0.026 |  | 0.019 | 0.01 | 0.001 | 2010-09-07 | 5.75 | 1.85 |  | 1.93 | 1.38 | 0.41 | 2010-09-07 | 4.4696 | 1.4054 |  | 0.98446 | 0.72464 | 0.2439
| 2010-09-13 | [6 empty] | 2010-09-13 | [6 empty] | 2010-09-13
| 2010-09-20 | 0.174 | 0.021 | 0.071 | 0.017 | 0.014 | 0.003 | 2010-09-20 | 4.92 | 1.69 | 3.59 | 1.92 | 1.69 | 0.6 | 2010-09-20 | 3.5366 | 1.2426 | 1.9777 | 0.88542 | 0.8284 | 0.5
| 2010-09-28 | 0.206 | 0.027 | 0.069 | 0.015 | 0.009 | 0.002 | 2010-09-28 | 4.62 | 1.83 | 2.97 | 1.48 | 1.17 | 0.43 | 2010-09-28 | 4.4589 | 1.4754 | 2.3232 | 1.0135 | 0.76923 | 0.46512
2010 upstream Inflows to River Murray | 2010-10-05 | 0.319 | 0.04 | 0.146 | 0.009 | 0.006 | 0.005 | 2010-10-05 | 7.27 | 2.44 | 5.08 | 1.3 | 1.11 | 0.53 | 2010-10-05 | 4.3879 | 1.6393 | 2.874 | 0.69231 | 0.54054 | 0.9434
| 2010-10-12 | 0.414 |  | 0.242 | 0.021 | 0.013 | 0.002 | 2010-10-12 | 9.25 |  | 7.62 | 2.06 | 1.64 | 0.48 | 2010-10-12 | 4.4757 |  | 3.1759 | 1.0194 | 0.79268 | 0.41667
| 2010-10-18 | 0.616 | 0.095 | 0.241 | 0.015 | 0.011 | 0.001 | 2010-10-18 | 9.47 | 4.61 | 7.83 | 2.07 | 1.63 | 0.65 | 2010-10-18 | 6.5048 | 2.0607 | 3.0779 | 0.72464 | 0.67485 | 0.15385
| 2010-10-25 | 0.402 | 0.06 | 0.285 | 0.022 | 0.014 | 0.002 | 2010-10-25 | 10.8 | 2.99 | 8.29 | 1.83 | 1.31 | 0.24 | 2010-10-25 | 3.7222 | 2.0067 | 3.4379 | 1.2022 | 1.0687 | 0.83333
| 2010-11-01 | 0.799 | 0.071 | 0.398 | 0.034 | 0.016 | 0.003 | 2010-11-01 | 13.6 | 4.06 | 10.7 | 2.83 | 1.67 | 0.54 | 2010-11-01 | 5.875 | 1.7488 | 3.7196 | 1.2014 | 0.95808 | 0.55556
| 2010-11-09 | 0.722 | 0.073 | 0.468 | 0.03 | 0.016 | 0.003 | 2010-11-09 | 14.7 | 4.25 | 12.43 | 2.67 | 1.88 | 0.33 | 2010-11-09 | 4.9116 | 1.7176 | 3.7651 | 1.1236 | 0.85106 | 0.90909
| 2010-11-16 | 0.72 |  | 0.397 | 0.038 | 0.021 | 0.002 | 2010-11-16 | 13.5 |  | 11.17 | 3.25 | 2.41 | 0.61 | 2010-11-16 | 5.3333 |  | 3.5542 | 1.1692 | 0.87137 | 0.32787
| 2010-11-22 | 0.578 |  | 0.306 | 0.034 | 0.019 | 0.001 | 2010-11-23 | 11.53 |  | 9.51 | 3.01 | 2.29 | 0.4 | 2010-11-23 | 5.013 |  | 3.2177 | 1.1296 | 0.82969 | 0.25
| 2010-11-29 | 0.717 | 0.078 | 0.264 | 0.034 | 0.036 | 0.007 | 2010-11-29 | 9.81 | 4.19 | 8.43 | 2.86 | 2.01 | 0.68 | 2010-11-29 | 7.3089 | 1.8616 | 3.1317 | 1.1888 | 1.791 | 1.0294
| 2010-12-06 | 0.705 | 0.105 | 0.321 | 0.031 | 0.014 | 0.001 | 2010-12-06 | 11.6 | 5.51 | 9.83 | 3 | 1.96 | 0.52 | 2010-12-06 | 6.0776 | 1.9056 | 3.2655 | 1.0333 | 0.71429 | 0.19231
| 2010-12-14 | 0.68 | 0.113 | 0.329 | 0.028 | 0.016 | 0.002 | 2010-12-14 | 11.7 | 5.7 | 10.08 | 2.49 | 2.1 | 0.59 | 2010-12-14 | 5.812 | 1.9825 | 3.2639 | 1.1245 | 0.7619 | 0.33898
| 2010-12-20 | 0.658 | 0.099 | 0.372 | 0.045 | 0.019 | 0.005 | 2010-12-20 | 12.63 | 5.73 | 11.17 | 4.09 | 2.3 | 0.5 | 2010-12-20 | 5.2098 | 1.7277 | 3.3303 | 1.1002 | 0.82609 | 1
| 2011-01-04 | 0.702 | 0.089 | 0.38 | 0.034 | 0.021 | 0.004 | 2011-01-04 | 13.1 | 5.01 | 11.27 | 2.99 | 2.52 | 0.66 | 2011-01-04 | 5.3588 | 1.7764 | 3.3718 | 1.1371 | 0.83333 | 0.60606
| 2011-01-10 | 0.682 | 0.088 | 0.433 | 0.06 | 0.025 | 0.003 | 2011-01-10 | 14.6 | 5.16 | 12.3 | 4.75 | 2.71 | 0.8 | 2011-01-10 | 4.6712 | 1.7054 | 3.5203 | 1.2632 | 0.92251 | 0.375
| 2011-01-17 | 0.716 | 0.145 | 0.477 | 0.062 | 0.025 | 0.002 | 2011-01-17 | 15.63 | 7.33 | 14 | 5.28 | 3.13 | 0.66 | 2011-01-17 | 4.5809 | 1.9782 | 3.4071 | 1.1742 | 0.79872 | 0.30303
| 2011-01-24 | 0.742 | 0.112 | 0.504 | 0.063 | 0.027 | 0 | 2011-01-24 | 16.73 | 6.46 | 14.93 | 5.3 | 3.32 | 0.73 | 2011-01-24 | 4.4351 | 1.7337 | 3.3758 | 1.1887 | 0.81325 | 0
| 2011-01-31 | 0.79 | 0.1 | 0.57 | 0.057 | 0.038 | 0.004 | 2011-01-31 | 18.53 | 5.93 | 16.43 | 4.67 | 3.83 | 0.44 | 2011-01-31 | 4.2634 | 1.6863 | 3.4693 | 1.2206 | 0.99217 | 0.90909
| 2011-02-07 | [6 empty] | 2011-02-07 | [6 empty] | 2011-02-07
| 2011-02-15 | 0.68 | 0.117 | 0.565 | 0.06 | 0.028 | 0.006 | 2011-02-15 | 19.1 | 6.66 | 17.1 | 5.66 | 3.45 | 0.78 | 2011-02-15 | 3.5602 | 1.7568 | 3.3041 | 1.0601 | 0.81159 | 0.76923
| 2011-02-25 | 0.606 |  | 0.515 | 0.061 | 0.031 | 0.006 | 2011-02-25 | 18.37 |  | 16 | 5.47 | 3.62 | 0.62 | 2011-02-25 | 3.2989 |  | 3.2188 | 1.1152 | 0.85635 | 0.96774
| 2011-02-28 | 0.604 | 0.132 | 0.514 | 0.063 | 0.019 | 0.008 | 2011-02-28 | 18.9 | 7.04 | 16.5 | 5.61 | 2.51 | 0.67 | 2011-02-28 | 3.1958 | 1.875 | 3.1152 | 1.123 | 0.75697 | 1.194
| 2011-03-07 | 0.609 | 0.166 | 0.56 | 0.061 | 0.036 | 0.008 | 2011-03-07 | 18.83 | 8.79 | 17.27 | 5.53 | 3.98 | 0.47 | 2011-03-07 | 3.2342 | 1.8885 | 3.2426 | 1.1031 | 0.90452 | 1.7021
| 2011-03-15 | 0.575 | 0.121 |  | 0.053 | 0.033 |  | 2011-03-15 | 17.9 | 7.38 |  | 5.67 | 4.06 |  | 2011-03-15 | 3.2123 | 1.6396 |  | 0.93474 | 0.81281
| 2011-03-21 | 0.467 | 0.114 | 0.361 | 0.041 | 0.028 | 0.009 | 2011-03-21 | 16.6 | 6.4 | 13.3 | 4.24 | 3.39 | 1.01 | 2011-03-21 | 2.8133 | 1.7812 | 2.7143 | 0.96698 | 0.82596 | 0.89109
| 2011-03-28 | 0.493 | 0.099 | 0.345 | 0.043 | 0.02 | 0.007 | 2011-03-28 | 16.6 | 6.44 | 12.6 | 4.61 | 3.04 | 0.6 | 2011-03-28 | 2.9699 | 1.5373 | 2.7381 | 0.93275 | 0.65789 | 1.1667
| 2011-04-04 | 0.533 | 0.086 | 0.356 | 0.035 | 0.021 | 0.003 | 2011-04-04 | 15.43 | 5.18 | 12.6 | 3.68 | 2.63 | 0.4 | 2011-04-04 | 3.4543 | 1.6602 | 2.8254 | 0.95109 | 0.79848 | 0.75
| 2011-04-11 | 0.427 | 0.077 | 0.362 | 0.033 | 0.025 | 0.001 | 2011-04-11 | 16.97 | 5.73 | 12.77 | 4.43 | 3.03 | 0.58 | 2011-04-11 | 2.5162 | 1.3438 | 2.8348 | 0.74492 | 0.82508 | 0.17241
| 2011-04-18 | 0.484 | 0.088 | 0.276 | 0.031 | 0.013 | 0.006 | 2011-04-18 | 13.5 | 5.35 | 10.7 | 3.23 | 1.77 | 0.5 | 2011-04-18 | 3.5852 | 1.6449 | 2.5794 | 0.95975 | 0.73446 | 1.2
| 2011-05-02 | 0.346 | 0.09 | 0.284 | 0.029 | 0.016 | 0.001 | 2011-05-02 | 12.5 | 5.5 | 10.67 | 3.54 | 2.61 | 0.43 | 2011-05-02 | 2.768 | 1.6364 | 2.6617 | 0.81921 | 0.61303 | 0.23256
| 2011-05-09 | 0.356 | 0.081 | 0.27 | 0.048 | 0.028 | 0.003 | 2011-05-09 | 11.23 | 5.16 | 9.92 | 4.15 | 3.16 | 0.29 | 2011-05-09 | 3.1701 | 1.5698 | 2.7218 | 1.1566 | 0.88608 | 1.0345
| 2011-05-16 | 0.311 | 0.069 | 0.264 | 0.044 | 0.03 | 0.002 | 2011-05-16 | 12.5 | 4.54 | 9.99 | 3.98 | 3.17 | 0.27 | 2011-05-16 | 2.488 | 1.5198 | 2.6426 | 1.1055 | 0.94637 | 0.74074
| 2011-05-23 | 0.351 | 0.111 | 0.247 | 0.031 | 0.018 | 0.002 | 2011-05-23 | 10.83 | 6.31 | 9.46 | 3.04 | 2.21 | 0.34 | 2011-05-23 | 3.241 | 1.7591 | 2.611 | 1.0197 | 0.81448 | 0.58824
| 2011-05-30 | 0.334 | 0.094 | 0.234 | 0.037 | 0.022 | 0.003 | 2011-05-30 | 10.23 | 5.51 | 9.01 | 3.27 | 2.58 | 0.35 | 2011-05-30 | 3.2649 | 1.706 | 2.5971 | 1.1315 | 0.85271 | 0.85714
| 2011-06-06 | 0.38 | 0.079 | 0.203 | 0.025 | 0.018 | 0.004 | 2011-06-06 | 9.97 | 4.95 | 8.47 | 2.53 | 2.08 | 0.43 | 2011-06-06 | 3.8114 | 1.596 | 2.3967 | 0.98814 | 0.86538 | 0.93023
| 2011-06-14 | 0.326 | 0.064 | 0.204 | 0.029 | 0.018 | 0.003 | 2011-06-14 | 8.98 | 4.09 | 8.33 | 2.75 | 2.02 | 0.56 | 2011-06-14 | 3.6303 | 1.5648 | 2.449 | 1.0545 | 0.89109 | 0.53571
| 2011-06-20 | [6 empty] | 2011-06-20 | [6 empty] | 2011-06-20
| 2011-06-27 | [6 empty] | 2011-06-27 | [6 empty] | 2011-06-27
| 2011-07-04 | [6 empty] | 2011-07-04 | [6 empty] | 2011-07-04
| 2011-07-11 | [6 empty] | 2011-07-11 | 7.08 | 2.67 | 5.02 | 1.66 | 1.31 | 0.27 | 2011-07-11
| 2011-07-18 | 0.193 | 0.039 | 0.131 | 0.01 | 0.01 | 0.001 | 2011-07-18 | 5.78 | 2.49 | 4.93 | 1.16 | 1.18 | 0.17 | 2011-07-18 | 3.3391 | 1.5663 | 2.6572 | 0.86207 | 0.84746 | 0.58824
| 2011-07-25 | 0.187 | 0.032 | 0.123 | 0.01 | 0.009 | 0.002 | 2011-07-25 | 5.15 | 2.12 | 4.37 | 1.24 | 1.24 | 0.3 | 2011-07-25 | 3.6311 | 1.5094 | 2.8146 | 0.80645 | 0.72581 | 0.66667
| 2011-08-01 | 0.209 | 0.04 | 0.1 | 0.009 | 0.009 | 0.002 | 2011-08-01 | 5.35 | 2.58 | 4.16 | 1.13 | 1.23 | 0.24 | 2011-08-01 | 3.9065 | 1.5504 | 2.4038 | 0.79646 | 0.73171 | 0.83333
| 2011-08-09 | 0.227 | 0.031 | 0.114 | 0.01 | 0.01 | 0.003 | 2011-08-09 | 5.75 | 2.06 | 4.33 | 0.96 | 1.05 | 0.25 | 2011-08-09 | 3.9478 | 1.5049 | 2.6328 | 1.0417 | 0.95238 | 1.2
| 2011-08-15 | 0.237 | 0.035 | 0.118 | 0.015 | 0.009 | 0.001 | 2011-08-15 | 5.69 | 2.25 | 4.42 | 1.39 | 1.11 | 0.3 | 2011-08-15 | 4.1652 | 1.5556 | 2.6697 | 1.0791 | 0.81081 | 0.33333
| 2011-08-22 | 0.242 | 0.038 | 0.125 | 0.006 | 0.006 | 0.003 | 2011-08-22 | 5.6 | 2.47 | 4.6 | 0.92 | 1.03 | 0.28 | 2011-08-22 | 4.3214 | 1.5385 | 2.7174 | 0.65217 | 0.58252 | 1.0714
| 2011-08-30 | 0.256 | 0.038 | 0.12 | 0.007 | 0.007 | 0.001 | 2011-08-30 | 5.48 | 2.29 | 4.21 | 0.89 | 0.93 | 0.34 | 2011-08-30 | 4.6715 | 1.6594 | 2.8504 | 0.78652 | 0.75269 | 0.29412
| 2011-09-05 | 0.256 | 0.045 | 0.127 | 0.01 | 0.009 | 0.002 | 2011-09-05 | 5.69 | 2.64 | 4.44 | 1.07 | 1.04 | 0.37 | 2011-09-05 | 4.4991 | 1.7045 | 2.8604 | 0.93458 | 0.86538 | 0.54054
| 2011-09-13 | 0.287 | 0.044 | 0.137 | 0.01 | 0.01 | 0.002 | 2011-09-13 | 6.03 | 2.55 | 6.42 | 1.02 | 1.07 | 0.28 | 2011-09-13 | 4.7595 | 1.7255 | 2.134 | 0.98039 | 0.93458 | 0.71429
| 2011-09-19 | 0.243 | 0.039 | 0.135 | 0.005 | 0.006 | 0 | 2011-09-19 | 5.97 | 2.45 | 4.62 | 0.8 | 0.89 | 0.25 | 2011-09-19 | 4.0704 | 1.5918 | 2.9221 | 0.625 | 0.67416 | 0
| 2011-09-26 | 0.284 | 0.037 | 0.131 | 0.005 | 0.005 | 0 | 2011-09-26 | 5.72 | 2.28 | 4.57 | 0.78 | 0.88 | 0.2 | 2011-09-26 | 4.965 | 1.6228 | 2.8665 | 0.64103 | 0.56818 | 0
| 2011-10-04 | 0.266 | 0.037 | 0.173 | 0.009 | 0.008 | 0.002 | 2011-10-04 | 7.2 | 2.25 | 5.58 | 1.09 | 1.08 | 1.11 | 2011-10-04 | 3.6944 | 1.6444 | 3.1004 | 0.82569 | 0.74074 | 0.18018
| 2011-10-10 | 0.366 | 0.057 | 0.188 | 0.016 | 0.016 | 0.002 | 2011-10-10 | 7.62 | 2.93 | 6.06 | 1.48 | 1.29 | 0.29 | 2011-10-10 | 4.8031 | 1.9454 | 3.1023 | 1.0811 | 1.2403 | 0.68966
| 2011-10-17 | 0.314 | 0.047 | 0.192 | 0.013 | 0.009 | 0.002 | 2011-10-17 | 7.42 | 2.71 | 6.21 | 1.21 | 1.08 | 0.24 | 2011-10-17 | 4.2318 | 1.7343 | 3.0918 | 1.0744 | 0.83333 | 0.83333
| 2011-10-25 | 0.3 | 0.062 | 0.191 | 0.014 | 0.011 | 0.002 | 2011-10-24 | 7.53 | 3.52 | 6.52 | 1.63 | 1.52 | 0.86 | 2011-10-25 | 3.9841 | 1.7614 | 2.9294 | 0.8589 | 0.72368 | 0.23256
| 2011-10-31 | 0.262 | 0.044 | 0.184 | 0.014 | 0.011 | 0.002 | 2011-10-31 | 7.4 | 2.69 | 6.32 | 1.39 | 1.34 | 0.35 | 2011-10-31 | 3.5405 | 1.6357 | 2.9114 | 1.0072 | 0.8209 | 0.57143
| 2011-11-07 | 0.28 | 0.044 | 0.186 | 0.017 | 0.013 | 0.002 | 2011-11-07 | 7.25 | 2.8 | 6.1 | 1.69 | 1.63 | 0.42 | 2011-11-07 | 3.8621 | 1.5714 | 3.0492 | 1.0059 | 0.79755 | 0.47619
| 2011-11-14 | 0.236 | 0.053 | 0.179 | 0.018 | 0.014 | 0.003 | 2011-11-14 | 6.83 | 3.02 | 6.02 | 1.56 | 1.52 | 0.38 | 2011-11-14 | 3.4553 | 1.755 | 2.9734 | 1.1538 | 0.92105 | 0.78947
| 2011-11-21 | 0.259 | 0.056 | 0.172 | 0.015 | 0.011 | 0.005 | 2011-11-21 | 6.99 | 3.21 | 6.15 | 1.52 | 1.34 | 1.62 | 2011-11-21 | 3.7053 | 1.7445 | 2.7967 | 0.98684 | 0.8209 | 0.30864
| 2011-11-28 | 0.2 | 0.065 | 0.168 | 0.016 | 0.013 | 0.002 | 2011-11-28 | 6.67 | 3.62 | 6.09 | 1.64 | 1.4 | 0.26 | 2011-11-28 | 2.9985 | 1.7956 | 2.7586 | 0.97561 | 0.92857 | 0.76923
| 2011-12-05 | 0.213 | 0.04 | 0.149 | 0.015 | 0.013 | 0.002 | 2011-12-05 | 6.26 | 2.59 | 5.39 | 1.4 | 1.38 | 0.28 | 2011-12-05 | 3.4026 | 1.5444 | 2.7644 | 1.0714 | 0.94203 | 0.71429
| 2011-12-12 | 0.177 | 0.039 | 0.136 | 0.012 | 0.01 | 0.002 | 2011-12-12 | 5.63 | 2.52 | 4.97 | 1.19 | 1.2 | 0.23 | 2011-12-12 | 3.1439 | 1.5476 | 2.7364 | 1.0084 | 0.83333 | 0.86957
| 2011-12-19 | 0.152 | 0.041 | 0.137 | 0.018 | 0.011 | 0.002 | 2011-12-19 | 5.53 | 2.62 | 5.15 | 1.62 | 1.49 | 0.26 | 2011-12-19 | 2.7486 | 1.5649 | 2.6602 | 1.1111 | 0.73826 | 0.76923
| 2011-12-26 | [6 empty] | 2011-12-26 | [6 empty] | 2011-12-26
| 2012-01-02 | 0.179 | 0.037 | 0.129 | 0.009 | 0.016 | 0.002 | 2012-01-02 | 5.81 | 2.44 | 4.96 | 1.14 | 1.57 | 0.53 | 2012-01-02 | 3.0809 | 1.5164 | 2.6008 | 0.78947 | 1.0191 | 0.37736
| 2012-01-09 | 0.161 | 0.043 | 0.125 | 0.008 | 0.008 | 0.001 | 2012-01-09 | 5.17 | 2.52 | 4.64 | 0.92 | 1.02 | 0.26 | 2012-01-09 | 3.1141 | 1.7063 | 2.694 | 0.86957 | 0.78431 | 0.38462
| 2012-01-16 | 0.139 | 0.046 | 0.132 | 0.005 | 0.009 | 0.003 | 2012-01-16 | 6.41 | 3.11 | 5.3 | 1 | 1.23 | 0.45 | 2012-01-16 | 2.1685 | 1.4791 | 2.4906 | 0.5 | 0.73171 | 0.66667
| 2012-01-23 | [6 empty] | 2012-01-23 | [6 empty] | 2012-01-23
| 2012-01-30 | [6 empty] | 2012-01-30 | [6 empty] | 2012-01-30
| 2012-02-06 | 0.163 | 0.073 | 0.148 | 0.013 | 0.011 | 0.001 | 2012-02-06 | 8.74 | 4.97 | 6.26 | 2.02 | 1.61 | 0.31 | 2012-02-06 | 1.865 | 1.4688 | 2.3642 | 0.64356 | 0.68323 | 0.32258
| 2012-02-13 | 0.198 | 0.067 | 0.157 | 0.027 | 0.012 | 0.001 | 2012-02-13 | 7.93 | 4.19 | 6.5 | 2.49 | 1.67 | 0.3 | 2012-02-13 | 2.4968 | 1.599 | 2.4154 | 1.0843 | 0.71856 | 0.33333
| 2012-02-20 | 0.221 | 0.053 | 0.201 | 0.013 | 0.013 | 0.003 | 2012-02-20 | 7.69 | 3.01 | 5.83 | 1.34 | 1.39 | 0.33 | 2012-02-20 | 2.8739 | 1.7608 | 3.4477 | 0.97015 | 0.93525 | 0.90909
| 2012-02-27 | 0.276 | 0.06 | 0.221 | 0.014 | 0.013 | 0.003 | 2012-02-27 | 9.08 | 3.47 | 6.76 | 1.62 | 1.39 | 0.71 | 2012-02-27 | 3.0396 | 1.7291 | 3.2692 | 0.8642 | 0.93525 | 0.42254
| 2012-03-05 | 0.304 | 0.058 | 0.21 | 0.026 | 0.015 | 0.002 | 2012-03-05 | 8.61 | 3.44 | 7.01 | 2.19 | 1.62 | 0.26 | 2012-03-05 | 3.5308 | 1.686 | 2.9957 | 1.1872 | 0.92593 | 0.76923
| 2012-03-12 | 0.422 | 0.064 | 0.212 | 0.013 | 0.012 | 0.002 | 2012-03-12 | 8.53 | 3.61 | 7.54 | 1.91 | 1.39 | 0.36 | 2012-03-12 | 4.9472 | 1.7729 | 2.8117 | 0.68063 | 0.86331 | 0.55556
| 2012-03-19 | 0.302 | 0.061 | 0.216 | 0.013 | 0.011 | 0.002 | 2012-03-19 | 8.99 | 3.57 | 7.94 | 1.82 | 1.4 | 0.24 | 2012-03-19 | 3.3593 | 1.7087 | 2.7204 | 0.71429 | 0.78571 | 0.83333
| 2012-03-26 | 0.275 | 0.075 | 0.228 | 0.017 | 0.013 | 0.003 | 2012-03-26 | 9.38 | 4.35 | 8.23 | 1.77 | 1.49 | 0.49 | 2012-03-26 | 2.9318 | 1.7241 | 2.7704 | 0.96045 | 0.87248 | 0.61224
| 2012-04-02 | 0.303 | 0.059 | 0.179 | 0.023 | 0.012 | 0.001 | 2012-04-02 | 7.9 | 3.43 | 6.34 | 2.14 | 1.58 | 0.3 | 2012-04-02 | 3.8354 | 1.7201 | 2.8233 | 1.0748 | 0.75949 | 0.33333
| 2012-04-09 | 0.334 | 0.057 | 0.228 | 0.016 | 0.009 | 0.001 | 2012-04-09 | 9 | 3.18 | 7.25 | 1.63 | 1.23 | 0.23 | 2012-04-09 | 3.7111 | 1.7925 | 3.1448 | 0.9816 | 0.73171 | 0.43478
| 2012-04-16 | 0.52 | 0.085 | 0.322 | 0.012 | 0.011 | 0.002 | 2012-04-16 | 11.6 | 4.42 | 9.14 | 1.26 | 1.38 | 0.38 | 2012-04-16 | 4.4828 | 1.9231 | 3.523 | 0.95238 | 0.7971 | 0.52632
| 2012-04-23 | 0.528 | 0.074 | 0.382 | 0.026 | 0.015 | 0.002 | 2012-04-23 | 12.3 | 4.11 | 10.37 | 2.15 | 1.6 | 0.27 | 2012-04-23 | 4.2927 | 1.8005 | 3.6837 | 1.2093 | 0.9375 | 0.74074
| 2012-04-30 | 0.57 | 0.072 | 0.413 | 0.02 | 0.014 | 0.002 | 2012-04-30 | 13.57 | 3.99 | 11.2 | 1.99 | 2.02 | 0.61 | 2012-04-30 | 4.2004 | 1.8045 | 3.6875 | 1.005 | 0.69307 | 0.32787
| 2012-05-07 | 0.471 | 0.074 | 0.408 | 0.031 | 0.014 | 0.004 | 2012-05-07 | 14.53 | 4.16 | 11.57 | 2.5 | 1.7 | 0.35 | 2012-05-07 | 3.2416 | 1.7788 | 3.5264 | 1.24 | 0.82353 | 1.1429
| 2012-05-15 | 0.502 | 0.072 | 0.416 | 0.021 | 0.012 | 0.003 | 2012-05-15 | 14.6 | 4.62 | 12.37 | 2.04 | 1.5 | 0.28 | 2012-05-15 | 3.4384 | 1.5584 | 3.363 | 1.0294 | 0.8 | 1.0714
| 2012-05-21 | 0.459 | 0.097 | 0.408 | 0.018 | 0.013 | 0.002 | 2012-05-21 | 13.6 | 5.39 | 11.63 | 1.71 | 1.48 | 0.28 | 2012-05-21 | 3.375 | 1.7996 | 3.5082 | 1.0526 | 0.87838 | 0.71429
| 2012-06-04 | 0.449 | 0.085 | 0.379 | 0.021 | 0.015 | 0.008 | 2012-06-04 | 12.13 | 4.48 | 10.09 | 1.94 | 1.54 | 0.36 | 2012-06-04 | 3.7016 | 1.8973 | 3.7562 | 1.0825 | 0.97403 | 2.2222
| 2012-06-12 | 0.456 | 0.082 | 0.274 | 0.03 | 0.017 | 0.006 | 2012-06-12 | 11.93 | 4.46 | 10.5 | 2.39 | 1.74 | 0.27 | 2012-06-12 | 3.8223 | 1.8386 | 2.6095 | 1.2552 | 0.97701 | 2.2222
| 2012-06-18 | 0.403 | 0.099 | 0.359 | 0.025 | 0.019 | 0.004 | 2012-06-18 | 12.2 | 5.19 | 10.17 | 2.11 | 1.8 | 0.26 | 2012-06-18 | 3.3033 | 1.9075 | 3.53 | 1.1848 | 1.0556 | 1.5385
| 2012-06-25 | 0.307 | 0.074 | 0.262 | 0.015 | 0.011 | 0.003 | 2012-06-25 | 10.3 | 4.13 | 8.61 | 1.51 | 1.22 | 0.25 | 2012-06-25 | 2.9806 | 1.7918 | 3.043 | 0.99338 | 0.90164 | 1.2
| 2012-07-02 | 0.306 | 0.083 | 0.251 | 0.033 | 0.018 | 0.003 | 2012-07-02 | 9.52 | 4.55 | 8.42 | 2.7 | 1.8 | 0.27 | 2012-07-02 | 3.2143 | 1.8242 | 2.981 | 1.2222 | 1 | 1.1111
| 2012-07-09 | 0.245 | 0.071 | 0.223 | 0.019 | 0.014 | 0.002 | 2012-07-09 | 8.32 | 4.13 | 7.3 | 1.89 | 1.64 | 0.24 | 2012-07-09 | 2.9447 | 1.7191 | 3.0548 | 1.0053 | 0.85366 | 0.83333
| 2012-07-16 | 0.239 | 0.064 | 0.21 | 0.013 | 0.012 | 0.003
| 2012-07-23 | 0.232 | 0.051 | 0.18 | 0.037 | 0.023 | 0.003
| 2012-07-31 | 0.188 | 0.038 | 0.145 | 0.024 | 0.014 | 0.004
Formulas:
DOC (mg/L C) = [DOC (mg/L C), row above]+7
UV @ 254nm (/cm) = [UV @ 254nm (/cm), row above]+7
SUVA (/m/mg/L) = [SUVA (/m/mg/L), row above]+7